## Slide 1: Radiation Heat Load and Coil Lifetime Calculations in Support of FRIB Magnet Design
Dali Georgobiani, Marc Hausmann, Mauricio Portillo, Earle Burkhardt, Georg Bollen
Facility for Rare Isotope Beams (FRIB) Michigan State University, East Lansing, MI 48824 USA

## Slide 2: Outline
  Brief introduction to FRIB
  Radiation transport scope within the project
Radiation transport analysis of the fragment separator magnets
  Examples of calculations for magnets exposed to high radiation levels
    Room temperature quadrupole magnet – coil lifetimes
    Superconducting quadrupole magnets – cryogenic component heat loads, coil lifetimes
    Superconducting dipole magnets – cryogenic component heat loads, coil lifetimes, poletip thermal analysis
Summary and conclusions

## Slide 3: Facility for Rare Isotope Beams A Future DOE-SC National User Facility
Funded by DOE–SC Office of Nuclear Physics with contributions and cost share from Michigan State University and State of Michigan
Serving over 1,300 users
Key feature is 400 kW beam power for all ions (5x1013 238U/s)
Separation of isotopes in-flight
  Fast development time for any isotope
  Suited for all elements and short half-lives
  Fast, stopped, and reaccelerated beams
Notes: $730M TPC,

## Slide 4: Radiation Transport Scope Technical Design and Safe Operation of Entire Project is Supported by Radiation Calculations
FRIB facility
  Accelerator Systems
  Experimental Systems
  Experimental areas
Technical scope
  Bulk, local shielding
  Component and material choices
  Hands-on, remote handling
  Personnel, public doses
Target facility model
  Encompasses pre-target beam delivery system (BDS) area, production target systems (hot cell), fragment separator
Rare isotope beams
400 kW beam (~ 100 kW at target, ~ 300 kW at beam dump)
1 W/m beam losses

## Slide 5: Fragment Separator
Three stage fragment separator for production and delivery of rare isotopes with high rates and high purities to maximize FRIB science reach
Primary beam power of 400 kW
  Beam energies of ≥ 200 MeV/u
Hot cell: High radiation environment
Two major sources: beam on target (100 kW) and on beam dump (300 kW)
Radiation heat loads to magnets produce doses of orders of several MGy
Magnet coil quenching, component lifetime concerns

## Slide 6: Radiation Transport Model High Level of Detail Supports Construction and Preparation for Operations
Calculations are based on models developed from mechanical and facility design
Model and materials are updated as the project progresses
  Updates are provided by mechanical design group and magnet systems department
    Capability of the models to transport ions in magnetic fields is important
  Magnetic fields correspond to those needed for beam optics and are provided by fragment separator group
Radiation transport model of the preseparator vacuum vessels
Q1
Q3
Q2
D1
M1
Target
Beam Dump
M2
D2
Q4
Q5
Q6
Q7
Wedge
Beam direction
3D engineering design of the preseparator vacuum vessels
Beam direction

## Slide 7: Hot Cell Magnets: Why Important?
Beam induced effects on superconducting magnets and other components are important to FRIB operations
  Power losses need to be removed efficiently
  Magnet heat loads drive water cooling and cryogenic component design
  Coil lifetimes depend on radiation doses
  Detailed power deposition information provided to the magnet designers and engineers for final magnet design
Beam optics modes affect the loss characteristics
  Requires beam physics and radiation transport calculations
  Optics modes developed to maximize rare isotopes to experiment yet minimize damage
Target
D1
Beam Dump
FRIB preseparator beam line elements
Wedge
D2
Q1, Q2, Q3, M1

## Slide 8: Room Temperature Quadrupole
Q1 coil design support
  First magnet after the target – high radiation environment
  Coils contain cyanate ester, therefore lifetime concerns
    Radiation tolerance 150 MGy
  Local shielding optimization:
    Shield in front of the magnet reduces coil heat loads 2-4 times
    Shield inside the magnet reduces coil heat loads 7 times
    Copper or other material
  Beam setting example: 48Ca, 261 MeV/u
    Light, neutron-rich beam; to be used frequently; a worst-case scenario
    Peak heat loads into coils ~ 5 mW/cc
      Coil lifetimes ~7 years
Copper filling
Q1 radiation transport model
3D engineering design of Q1

## Slide 9: Q1 Coil Heat Loads: Various Beams
Beam | Annual Time, % | Coil Lifetime, years | Total Weighted Lifetime, years
Oxygen-16 | 5 | 5 | 30 (similar to facility lifetime)
Calcium-48 | 21 | 7 | 
Krypton-86 | 27 | 20 | 
Xenon-136 | 12 | 30 | 
Uranium-238 | 35 | 48 | 
FRIB to operate with many beam scenarios
  Heat loads calculated for 5 beams planned to be used most often
  Coil lifetimes range from
    5 years (16O, 213 MeV/u) to
    48 years (238U, 203 MeV/u)
  Annual-time-weighted lifetime is ~30 years
  Planned FRIB facility lifetime is 30 years
Heat Load (W/cc)
Inner Coils
Heat Load (W/cc)
Front Coils

## Slide 10: Superconducting Quadrupoles
Q2 & Q3 cryogenic component design support
  Heat loads into cryogenically cooled components calculated
  Analysis supports cryogenic cooling design finalization
  Local shielding suggested, optimized as needed
  Worst-case scenarios considered
  Beam setting example: 48Ca, 261 MeV/u
Q2 radiation transport model
Cryostat
Yoke
Coils
He
Thermal shield
Heat loads into cryogenic components
3D engineering design of Q2

## Slide 11: Q2 Coil Lifetime Estimates
Heat Load (W/cc)
Heat Load (W/cc)
Heat Load (W/cc)
Heat Load (W/cc)
Closest to target -> -> -> Farthest from target
Q2 & Q3 coil design support
  Peak heat loads into coils need to be reduced
    To avoid quenching
    To increase coil lifetimes (SC coils contain cyanate ester, Kapton)
  Peak heat loads: Corrector coils at the magnet front
    ~ 20 mW/cc or ~ 2 years coil lifetime for a 48Ca, 261 MeV/u beam
  Heat load major contributors: Protons (~50%), other light charged particles
  Placing 5 cm thick copper or hevimet shield between Q1 and Q2:
    ~ 2 - 3 times lower peak heat loads

## Slide 12: Superconducting Dipoles
First 30°dipole design support
  Benchmark cases defined having potential for the most extreme conditions on the magnets
  Oxygen primary beams tend to pose the most extremes
    Large fraction of the beam reacts
    Products and primary beam characterized by some of the highest phase spaces after the target
  Calcium primary beams also analyzed
    Are also neutron-rich light beams
    And will be used relatively often
  Uranium primary beam produces much less heat load and damage
Most of the time, we expect to run different beams that do not present extreme cases in terms of heat loads
Coils
Poletips
Copper blockers
D1 radiation transport model
3D engineering design of D1

## Slide 13: Dipole Component Heat Loads
Dipole cryogenic component heat loads study
  Supports cryogenic system design verification
  Several worst-case beams studied
  Examples: 2 settings of 48Ca at 261 MeV/u
    Close to primary beam rigidity (center), => 31Al
    High rigidity (low), => 40Mg
Dipole coil heat loads, lifetimes
  Same beams, settings
  Peak heat load 14 (29) mW/cc
  Coil lifetimes 3 (2) years
  Local shielding considered
Heat Load (W/cc)
Max 1 W/cc
Heat Load (W/cc)
Max 11 W/cc
D1 dipole poletip heat load maps
Total 0.5 kW
Total 6 kW
Heat Load (W/cc)
D1 front coil heat load maps
Dipole cryogenic part heat loads

## Slide 14: Hot Cell Magnet Detailed Radiation Studies Thermal Analysis for 30°Dipole Poletips
Heat loads in water cooled dipole poletips
  A worst-case beam 16O, 313 MeV/u, => 9C
    Total heat load into poletips = 3 kW
    Water cooling - 2 gpm flow rate
    Poletips: Tmax = 50 ºC
    Cooling water: Tmax = 40 ºC
  Another worst-case beam 48Ca, 261 MeV/u, => 40Mg
    Total heat load into poletips = 9 kW
    Water cooling – 8.5 gpm flow rate
    Poletips: Tmax = 67 ºC
    Cooling water: Tmax = 45 ºC
    But if flow rate is 4.25 gpm then
    Poletips: Tmax = 77 ºC
Temperatures are reasonably low and should not affect magnetic field homogeneity appreciably
Poletip simple model
Heat Load (W/cc)
Poletip heat map
Total 3 kW
Copper
Water channels
Area with highest power density
Poletip thermal map

## Slide 15: Summary and Conclusions
  FRIB being designed and established at MSU as a national user facility to provide fast, stopped, and reaccelerated beams of rare isotopes
High radiation environment in the project target facility with fragment separator demands detailed analysis of radiation heat loads to beam line components, particularly magnets
Various studies of the magnets exposed to the highest radiation levels performed, component heat loads analyzed
  Calculations presented are part of a multi-step, iterative process to validate detailed beam line component designs and support future operations within the facility

## Slide 16: References
Monte Carlo particle transport codes PHITS and MCNPX, visualization software VISED, and conversion software MCAM were used
  PHITS: T. Sato, K. Niita, N. Matsuda, S. Hashimoto, Y. Iwamoto, S. Noda, T. Ogawa, H. Iwase, H. Nakashima, T. Fukahori, K. Okumura, T. Kai, S. Chiba, T. Furuta and L. Sihver, Particle and Heavy Ion Transport Code System PHITS, Version 2.52, J. Nucl. Sci. Technol. 50:9, 913-923 (2013)
  MCNPX: D. B. Pelowitz, ed., MCNPX User's Manual, Version 2.7.0, Los Alamos National Laboratory report LA-CP-11-00438 (2011)
  VISED: http://www.mcnpvised.com/
  MCAM: Y. Wu, FDS Team, CAD-based interface programs for fusion neutron transport simulation, Fusion Engineering and Design 84 (2009) 1987-1992

## Slide 17: Acknowledgements
I would like to express my gratitude to the SATIF-13 organizers…
…To my colleagues at FRIB for all their help and guidance…
…And to fellow participants for their attention!
This material is based on work supported by the U.S. Department of Energy Office of Science under Cooperative Agreement DE-SC0000661, the State of Michigan and Michigan State University. Michigan State University designs and establishes FRIB as a DOE Office of Science National User Facility in support of the mission of the Office of Nuclear Physics.

## Slide 18: Radiation Protection Limits
Meet regulatory limits and MSU ALARA (As Low as Reasonably Achievable) limits for general public and radiation workers (Regulatory Requirements, R10103-TD-000014, 13 April 2010)
The site is under NRC license**
Radiation Dose – Worker | Standard*: 5,000 mrem/yr MSU ALARA Goal**: 500 mrem/yr | 
Radiation Dose – Public | Standard*: 100 mrem/yr and < 2 mrem/(any one hour) MSU ALARA Goal**: 10 mrem/yr and < 2 mrem/(any one hour) | 
Air - maximum exposure to nearest receptor | Standard*: 10 mrem/y MSU ALARA Goal**: 1 mrem/yr | 
Groundwater – effluent | 3H Standard*: 1,000 pCi/ml FRIB Design Goal: 20 pCi/ml (drinking water standard***) | 22Na Standard*: 6 pCi/ml FRIB Design Goal: 0.4 pCi/ml (drinking water standard***)
* Standard refers to 10 CFR 20 (Nuclear Regulatory Commission)
** MSU ALARA – NRC License Number 21-00021-29, MSU Type A Broad Scope License. MSU operates as a fully-licensed, non fuel cycle R&D Type A, NRC broad-scope licensee since 1977
*** Standard refers to 40 CFR 141 (Environmental Protection Agency)